# RCA Data Elements

## 1. High-Frequency Operational Process Data (Primary Observables)

These are the raw physical signals.

Data Elements

- Analog process variables (pressure, temperature, flow, level)

- Neutron flux (source, intermediate, power range)

- Vibration data (rotating equipment)

- Electrical parameters (voltage, current, frequency)

- Valve positions (% open)

- Damper positions

- Pump speeds

- Control rod positions

- Derived signals (calculated parameters)

- Setpoints (current and historical)

Metadata Required

- Tag name

- Instrument ID

- System / subsystem

- Safety classification

- Sampling rate

- Engineering units

- Calibration date

- Range limits

- Signal quality flags

Sources

- Process historian (e.g., PI)

- DCS archives

- Plant computer

- Vibration monitoring systems

- Digital I&C logs

These form the backbone of:

- Drift detection

- Changepoint detection

- First-out analysis

- Degradation monitoring

## 2. Discrete Event & Protection System Data (Causal Anchors)

These define state changes and protective actions.

Data Elements

- Breaker open/close transitions

- Relay actuations

- Trip signals (reactor trip, turbine trip)

- ESF actuation signals

- Interlock status changes

- Permissive state changes

- Alarm timestamps

- First-out logic records

- Sequence of events (SOE) logs (millisecond resolution)

Metadata Required

- Signal origin

- Logic association (trip, permissive, interlock)

- Safety function mapping

- Train designation (A/B)

Sources

- Protection system logs

- Sequence of Events Recorder

- Alarm management system

- Annunciator systems

Critical for:

- Timeline reconstruction

- Defense-in-depth mapping

- Causal directionality

## 3. Alarm System Data (Cognitive Load Layer)

Alarms are not just signals — they are filtered indicators.

Data Elements

- Alarm ID

- Alarm priority

- Alarm message text

- Timestamp (activation & clearing)

- Acknowledgment time

- Suppression state

- Shelving status

Sources

- Alarm management system

- DCS alarm archives

Needed for:

- Alarm clustering

- Flood detection

- Operator cognitive load assessment

- First meaningful signal identification

## 4. Maintenance & Work Management Data (Latent Contributors)

These are often root or contributing causes.

Data Elements

- Work orders

- Maintenance type (corrective, preventive)

- Equipment serviced

- Start/finish timestamps

- Deficiency codes

- Parts replaced

- Post-maintenance test results

- Deferred maintenance items

- Backlog status

Sources

- CMMS (e.g., Maximo, SAP)

- Work control center databases

Critical for:

- Change analysis

- Human performance contributors

- Maintenance-induced failures

- Latent condition identification

## 5. Configuration & Design Basis Data (Truth Model)

Without this, topology modeling fails.

Data Elements

- System boundaries

- P&IDs

- Single-line diagrams

- Equipment hierarchy

- Safety function definitions

- Redundancy mappings

- Train independence assumptions

- Setpoint design values

- Design basis documents

- Engineering change notices (ECNs)

Sources

- Engineering document management system

- Design basis repository

- Configuration management system

Critical for:

- Topology graph construction

- Defense-in-depth evaluation

- PRA integration

- Correct interpretation of protection logic

## 6. Corrective Action Program (CAP) & RCA Reports

Institutional memory layer.

Data Elements

- Condition reports

- Root cause statements

- Contributing causes

- Apparent causes

- Corrective actions

- Effectiveness reviews

- Significance level

- Human performance codes

- Causal factor charts

- Narrative descriptions

Sources

- CAP database

- Historical RCA archives

Used for:

- NLP semantic search

- Similarity matching

- Failure taxonomy learning

- Corrective action benchmarking

## 7. Industry Operating Experience (OE)

Fleet-wide intelligence.

Data Elements

- External event descriptions

- NRC event reports

- INPO OE documents

- Vendor bulletins

- Fleet event summaries

- Equipment reliability reports

Sources

- NRC public reports

- INPO databases

- EPRI databases

- Internal fleet OE systems

Used for:

- Cross-plant similarity detection

- Emerging failure mode detection

- Rare-event contextualization

## 8. Human Performance & Operations Data

Often overlooked, but critical.

Data Elements

- Operator logs

- Shift narratives

- Procedure steps performed

- Procedure revision history

- Control room recorder data (if applicable)

- Training records (role-based)

- Human performance evaluation tags

- Operator acknowledgment timing

Sources

- Operations logs

- Procedure management system

- Learning management systems

Supports:

- Deviation analysis

- Cognitive load correlation

- Latent organizational factors

## 9. Surveillance & Testing Data

Reveals hidden degradation.

Data Elements

- Surveillance test results

- Acceptance criteria

- As-found vs as-left values

- Trend over cycles

- Functional test outcomes

- Calibration results

Sources

- Test database

- I&C calibration systems

Critical for:

- Drift detection

- Latent condition detection

- Precursor identification

## 10. Environmental & External Data

Often causal in subtle ways.

Data Elements

- Ambient temperature

- Humidity

- Grid disturbances

- Switchyard events

- Seismic data

- Extreme weather

- Intake water conditions

Sources

- Meteorological systems

- Grid operator logs

- Plant environmental monitoring systems

Important for:

- Common-cause screening

- External event classification

## 11. PRA / Risk Model Data (Strategic Layer)

For future integration.

Data Elements

- Event trees

- Fault trees

- Basic event probabilities

- Safety function mapping

- Core damage frequency contribution

- Barrier definitions

Sources

- PRA software models

- Risk assessment databases

Supports:

- Risk significance evaluation

- Prioritization logic

## 12. Derived / Analytical Data (System-Generated)

Your tool will generate new data objects:

- Anomaly scores

- Changepoint markers

- Hypothesis sets

- Confidence scores

- Evidence linkage maps

- Timeline reconstructions

- Bias flags

- Alternative hypothesis rankings

These must be treated as first-class version-controlled artifacts.

## Cross-Cutting Metadata Requirements (Critical)

For every data source:

- Timestamp (with precision and timezone)

- Source system identifier

- Version number

- Data quality indicator

- Security classification

- Safety significance category

- Configuration baseline reference

Without consistent metadata strategy, fusion will fail.

## Analysis of RCA data elements

### Priority Value Schema

We’ll score each data source across 6 dimensions.

Each dimension: 1 (low) – 5 (high)

| Dimension | Meaning |
| --- | --- |
| RCA Impact (RI) | How critical this data is to identifying root causes |
| Frequency of Use (FU) | How often engineers rely on this data in real RCAs |
| Time Sensitivity (TS) | Required for rapid troubleshooting vs deep forensic only |
| Integration Feasibility (IF) | Technical difficulty of integration (5 = easy) |
| Data Quality Maturity (DQ) | Current cleanliness, structure, reliability |
| Regulatory Sensitivity (RS) | 5 = highly sensitive / controlled access |

### Composite Priority Score

For Phase 1 prioritization:

Priority=(2*RI+FU+TS+IF+DQ)-RSPriority = (2*RI + FU + TS + IF + DQ) - RSPriority=(2*RI+FU+TS+IF+DQ)-RS

Why subtract RS?
Highly sensitive sources may require cybersecurity or governance overhead and should be sequenced deliberately.

A. Core Operational Data

| Category | Data Source | RI | FU | TS | IF | DQ | RS | Priority | Phase Candidate |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Process Data | Historian (PI/DCS) | 5 | 5 | 5 | 4 | 4 | 3 | 20 | Phase 1 |
| Protection Events | SOE Recorder | 5 | 5 | 5 | 3 | 4 | 4 | 19 | Phase 1 |
| Alarm Logs | Alarm Management System | 5 | 5 | 5 | 4 | 4 | 3 | 20 | Phase 1 |
| Setpoints | Protection/DCS Config | 4 | 4 | 4 | 3 | 4 | 4 | 15 | Phase 1 |

B. Maintenance & Change Data

| Category | Data Source | RI | FU | TS | IF | DQ | RS | Priority | Phase |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Work Orders | CMMS (Maximo/SAP) | 5 | 4 | 3 | 3 | 3 | 3 | 16 | Phase 1 |
| ECNs | Engineering Change System | 4 | 3 | 2 | 2 | 3 | 3 | 12 | Phase 2 |
| Calibration Data | I&C Calibration DB | 4 | 3 | 2 | 3 | 3 | 3 | 13 | Phase 2 |
| Surveillance Tests | Test Tracking System | 4 | 3 | 2 | 3 | 3 | 3 | 13 | Phase 2 |

C. Institutional Knowledge

| Category | Data Source | RI | FU | TS | IF | DQ | RS | Priority | Phase |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CAP Database | Condition Reports | 5 | 4 | 2 | 3 | 2 | 4 | 14 | Phase 2 |
| RCA Reports | Historical RCA Archive | 5 | 4 | 2 | 3 | 2 | 4 | 14 | Phase 2 |
| Industry OE | NRC / INPO Reports | 4 | 3 | 1 | 2 | 2 | 3 | 10 | Phase 3 |

D. Design & Topology

| Category | Data Source | RI | FU | TS | IF | DQ | RS | Priority | Phase |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Equipment Hierarchy | Asset Registry | 5 | 4 | 3 | 3 | 4 | 3 | 17 | Phase 1 |
| P&IDs | Document Mgmt System | 4 | 4 | 2 | 2 | 3 | 3 | 12 | Phase 2 |
| Protection Logic | Relay Logic Database | 5 | 4 | 4 | 2 | 3 | 4 | 15 | Phase 2 |
| Safety Function Mapping | Design Basis Docs | 5 | 3 | 2 | 2 | 3 | 4 | 14 | Phase 3 |

E. Human Performance & Operations

| Category | Data Source | RI | FU | TS | IF | DQ | RS | Priority | Phase |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Operator Logs | Shift Narratives | 4 | 3 | 3 | 3 | 2 | 4 | 12 | Phase 2 |
| Procedure History | Procedure Mgmt System | 3 | 3 | 1 | 2 | 3 | 3 | 8 | Phase 3 |
| Training Records | LMS | 2 | 2 | 1 | 2 | 3 | 5 | 3 | Phase 3 |

### Interpretation

Phase 1 (Foundation – High Impact / High Feasibility)

- Historian data

- Alarm logs

- SOE recorder

- Equipment hierarchy

- CMMS work orders

- Setpoints

These enable:

- Timeline reconstruction

- Alarm clustering

- First-out detection

- Basic change analysis

- Drift detection

This alone delivers major value.

Phase 2 (Analytical Depth)

- CAP NLP retrieval

- RCA archives

- Surveillance & calibration trends

- Protection logic integration

- Operator logs

This is where causal reasoning strengthens.

Phase 3 (Strategic / Advanced Integration)

- PRA coupling

- Full safety function mapping

- Industry-wide OE mining

- Organizational contributors

### Observations From This Exercise

- You cannot build topology modeling until asset hierarchy and configuration management are stable.

- NLP over CAP should not be Phase 1 — too much integration overhead.

- SOE + Alarm + Historian = immediate high ROI.

- Regulatory sensitivity will affect deployment sequencing.

- Protection logic modeling is high impact but technically difficult.

### Important Strategic Insight

Architecture should be driven by the highest-priority Phase 1 data sources, not by the entire long-term vision.

Your architecture must:

- Ingest high-frequency time series

- Handle event streams

- Align multi-resolution timestamps

- Store derived analytical artifacts

- Maintain version control

Everything else layers on top.